## reckoner
HS650
Calculation of % oxygen remaining following a leak, spill or release of liquid nitrogen (Cryogen)
The following scenario automatically calculates the remaining percentage of oxygen in a room when a leak, spill or release of liquid nitrogen turns into a gas at room temperature.
The scenario addresses the worst case: that all the liquid nitrogen is converted from liquid to gas and displaces an equal volume of oxygen.
Enter your room volume in cubic metres (ie Length X Breadth X Height) : |  | 455 | m3
Enter the total liquid capacity in litres of all liquid nitrogen containing vessels in the room:
|  | 12 | L
Nitrogen liquid to gas conversion factor: | 0.682 | (at 15°C, and atmospheric pressure 101.325 kPa)
Normal % of oxygen (O2) in air: | 20.95 | %
The % Oxygen in the remaining air is: |  | 20.6223 | % | SAFE
Risk Controls
Consider external storage
Keep vessel sizes and number of vessels to a minimum
Consider mechanical extraction at sufficient rate to keep Oxygen above 19.5%
If storage is indoors, locate against external wall with louvered doors to outside air
Consider the need for ventilation failure alarm or O2 alarm or both

## IF Calculator is not working
HS650 should work
If it fails to work on you spreadsheet then you may need to turn on auto calculations – go to formula’s then calculate options select automatic.